## Instruction
Introduction:
- All communication is based on the Sunspec Modbus standard. Please refer to the official documentation of Sunspec Alliance: https://sunspec.org/sunspec-modbus-home/
- The unit ID is set to 1.
- A maximum of two parallel transactions with varying T-Ids is allowed.
- Values arching over multiple registers (e.g. Model 103, Evt1, bitfield32) have to be polled completely. It is not allowed to poll only the upper or lower 16 Bits.
- For reactive power control only one of the registers 123.OutPFSet_Ena, 123.VArPct_Ena, 126.ModEna and 131.ModEna can be activated. To change the mode, the current mode must be de-activated first.
- Except of model 123 (Immediate Inverter Controls) all data is written to flash memory - i.e. excessive write access can damage the device.
- As the data in model 123 is stored in RAM, it does not get restored after inverter shutdown. Cyclical writing is required.
- Loss of PV power in the evening can lead to restart of the AC aux supply and a short termination of Modbus communication.
- For the reading or writing of Modbus registers, use the register numbers reduced by the offset 1 in each case.

## 1
Address | Point | Type | Subvalue | Value | R/W | Conformance Notes
40003 | ID | uint16 |  | 1
40004 | L | uint16 |  | 66
40005 | Manufacturer (Mn) | string |  | SMA | R
40021 | Model (Md) | string |  | STP 110-60 | R
40037 | Options (Opt) | string |  |  | R
40045 | Version (Vr) | string |  | 1.00.16.S | R
40053 | Serial Number (SN) | string |  | A2004250015 | R
40069 | Device Address (DA) | uint16 |  | 1 | RW
40070 | Pad | pad |  |  | R

## 103
Address | Point | Type | Subvalue | Value | R/W | Conformance Notes
40071 | ID | uint16 |  | 103
40072 | L | uint16 |  | 50
40073 | Amps (A) | uint16 |  | supported | R
40074 | Amps PhaseA (AphA) | uint16 |  | supported | R
40075 | Amps PhaseB (AphB) | uint16 |  | supported | R
40076 | Amps PhaseC (AphC) | uint16 |  | supported | R
40077 | A_SF | sunssf |  | -1 | R
40078 | Phase Voltage AB (PPVphAB) | uint16 |  | supported | R
40079 | Phase Voltage BC (PPVphBC) | uint16 |  | supported | R
40080 | Phase Voltage CA (PPVphCA) | uint16 |  | supported | R
40081 | Phase Voltage AN (PhVphA) | uint16 |  | supported | R
40082 | Phase Voltage BN (PhVphB) | uint16 |  | supported | R
40083 | Phase Voltage CN (PhVphC) | uint16 |  | supported | R
40084 | V_SF | sunssf |  | -1 | R
40085 | Watts (W) | int16 |  | supported | R
40086 | W_SF | sunssf |  | 1 | R
40087 | Hz | uint16 |  | supported | R
40088 | Hz_SF | sunssf |  | -2 | R
40089 | VA | int16 |  | supported | R
40090 | VA_SF | sunssf |  | 1 | R
40091 | VAr | int16 |  | supported | R
40092 | VAr_SF | sunssf |  | 1 | R
40093 | PF | int16 |  | supported | R
40094 | PF_SF | sunssf |  | -3 | R
40095 | WattHours (WH) | acc32 |  | supported | R
40097 | WH_SF | sunssf |  | 2 | R
40098 | DC Amps (DCA) | uint16 |  | supported | R
40099 | DCA_SF | sunssf |  | -1 | R
40100 | DC Voltage (DCV) | uint16 |  | supported | R
40101 | DCV_SF | sunssf |  | -1 | R
40102 | DC Watts (DCW) | int16 |  | supported | R
40103 | DCW_SF | sunssf |  | 2 | R
40104 | Cabinet Temperature (TmpCab) | int16 |  | supported | R
40105 | Heat Sink Temperature (TmpSnk) | int16 |  | unimplemented | R
40106 | Transformer Temperature (TmpTrns) | int16 |  | unimplemented | R
40107 | Other Temperature (TmpOt) | int16 |  | unimplemented | R
40108 | Tmp_SF | sunssf |  | -1 | R
40109 | Operating State (St) | enum16 |  | supported | R
|  |  | Off (OFF) | supported
|  |  | Sleeping (SLEEPING) | supported
|  |  | Starting (STARTING) | supported
|  |  | MPPT | supported
|  |  | Throttled (THROTTLED) | supported
|  |  | Shutting down (SHUTTING_DOWN) | supported
|  |  | Fault (FAULT) | supported
|  |  | Standby (STANDBY) | supported
40110 | Vendor Operating State (StVnd) | enum16 |  | unimplemented | R
40111 | Event1 (Evt1) | bitfield32 |  | supported | R
|  |  | Ground fault (GROUND_FAULT) | supported
|  |  | DC over voltage (DC_OVER_VOLT) | supported
|  |  | AC disconnect open (AC_DISCONNECT) | supported
|  |  | DC disconnect open (DC_DISCONNECT) | supported
|  |  | Grid shutdown (GRID_DISCONNECT) | supported
|  |  | Cabinet open (CABINET_OPEN) | supported
|  |  | Manual shutdown (MANUAL_SHUTDOWN) | supported
|  |  | Over temperature (OVER_TEMP) | supported
|  |  | Frequency above limit (OVER_FREQUENCY) | supported
|  |  | Frequency under limit (UNDER_FREQUENCY) | supported
|  |  | AC Voltage above limit (AC_OVER_VOLT) | supported
|  |  | AC Voltage under limit (AC_UNDER_VOLT) | supported
|  |  | Blown String fuse on input (BLOWN_STRING_FUSE) | supported
|  |  | Under temperature (UNDER_TEMP) | supported
|  |  | Generic Memory or Communication error (internal) (MEMORY_LOSS) | supported
|  |  | Hardware test failure (HW_TEST_FAILURE) | supported
40113 | Event Bitfield 2 (Evt2) | bitfield32 |  | supported | R
40115 | Vendor Event Bitfield 1 (EvtVnd1) | bitfield32 |  | unimplemented | R
40117 | Vendor Event Bitfield 2 (EvtVnd2) | bitfield32 |  | unimplemented | R
40119 | Vendor Event Bitfield 3 (EvtVnd3) | bitfield32 |  | unimplemented | R
40121 | Vendor Event Bitfield 4 (EvtVnd4) | bitfield32 |  | unimplemented | R

## 120
Address | Point | Type | Subvalue | Value | R/W | Conformance Notes
40123 | ID | uint16 |  | 120
40124 | L | uint16 |  | 26
40125 | DERTyp | enum16 |  | supported | R
|  |  | PV | supported
|  |  | PV_STOR | supported
40126 | WRtg | uint16 |  | supported | R
40127 | WRtg_SF | sunssf |  | 2 | R
40128 | VARtg | uint16 |  | supported | R
40129 | VARtg_SF | sunssf |  | 2 | R
40130 | VArRtgQ1 | int16 |  | supported | R
40131 | VArRtgQ2 | int16 |  | supported | R
40132 | VArRtgQ3 | int16 |  | supported | R
40133 | VArRtgQ4 | int16 |  | supported | R
40134 | VArRtg_SF | sunssf |  | 2 | R
40135 | ARtg | uint16 |  | supported | R
40136 | ARtg_SF | sunssf |  | -1 | R
40137 | PFRtgQ1 | int16 |  | supported | R
40138 | PFRtgQ2 | int16 |  | supported | R
40139 | PFRtgQ3 | int16 |  | supported | R
40140 | PFRtgQ4 | int16 |  | supported | R
40141 | PFRtg_SF | sunssf |  | -3 | R
40142 | WHRtg | uint16 |  | unimplemented | R
40143 | WHRtg_SF | sunssf |  | unimplemented | R
40144 | AhrRtg | uint16 |  | unimplemented | R
40145 | AhrRtg_SF | sunssf |  | unimplemented | R
40146 | MaxChaRte | uint16 |  | unimplemented | R
40147 | MaxChaRte_SF | sunssf |  | unimplemented | R
40148 | MaxDisChaRte | uint16 |  | unimplemented | R
40149 | MaxDisChaRte_SF | sunssf |  | unimplemented | R
40150 | Pad | pad |  |  | R

## 121
Address | Point | Type | Subvalue | Value | R/W | Conformance Notes
40151 | ID | uint16 |  | 121
40152 | L | uint16 |  | 30
40153 | WMax | uint16 |  | supported | RW
40154 | VRef | uint16 |  | supported | RW
40155 | VRefOfs | int16 |  | supported | RW
40156 | VMax | uint16 |  | unimplemented | RW
40157 | VMin | uint16 |  | unimplemented | RW
40158 | VAMax | uint16 |  | supported | RW
40159 | VArMaxQ1 | int16 |  | unimplemented | RW
40160 | VArMaxQ2 | int16 |  | unimplemented | RW
40161 | VArMaxQ3 | int16 |  | unimplemented | RW
40162 | VArMaxQ4 | int16 |  | unimplemented | RW
40163 | WGra | uint16 |  | supported | RW
40164 | PFMinQ1 | int16 |  | unimplemented | RW
40165 | PFMinQ2 | int16 |  | unimplemented | RW
40166 | PFMinQ3 | int16 |  | unimplemented | RW
40167 | PFMinQ4 | int16 |  | unimplemented | RW
40168 | VArAct | enum16 |  | unimplemented | RW
|  |  | SWITCH | supported
|  |  | MAINTAIN | supported
40169 | ClcTotVA | enum16 |  | unimplemented | RW
|  |  | VECTOR | supported
|  |  | ARITHMETIC | supported
40170 | MaxRmpRte | uint16 |  | supported | RW
40171 | ECPNomHz | uint16 |  | supported | RW
40172 | ConnPh | enum16 |  | unimplemented | RW
|  |  | A | supported
|  |  | B | supported
|  |  | C | supported
40173 | WMax_SF | sunssf |  | 2 | R
40174 | VRef_SF | sunssf |  | 0 | R
40175 | VRefOfs_SF | sunssf |  | 0 | R
40176 | VMinMax_SF | sunssf |  | unimplemented | R
40177 | VAMax_SF | sunssf |  | 2 | R
40178 | VArMax_SF | sunssf |  | unimplemented | R
40179 | WGra_SF | sunssf |  | -1 | R
40180 | PFMin_SF | sunssf |  | unimplemented | R
40181 | MaxRmpRte_SF | sunssf |  | 0 | R
40182 | ECPNomHz_SF | sunssf |  | 0 | R

## 122
Address | Point | Type | Subvalue | Value | R/W | Conformance Notes
40183 | ID | uint16 |  | 122
40184 | L | uint16 |  | 44
40185 | PVConn | bitfield16 |  | supported | R
|  |  | CONNECTED | supported
|  |  | AVAILABLE | supported
|  |  | OPERATING | supported
|  |  | TEST | supported
40186 | StorConn | bitfield16 |  | unimplemented | R
|  |  | CONNECTED | supported
|  |  | AVAILABLE | supported
|  |  | OPERATING | supported
|  |  | TEST | supported
40187 | ECPConn | bitfield16 |  | supported | R
|  |  | CONNECTED | supported
40188 | ActWh | acc64 |  | supported | R
40192 | ActVAh | acc64 |  | unimplemented | R
40196 | ActVArhQ1 | acc64 |  | unimplemented | R
40200 | ActVArhQ2 | acc64 |  | unimplemented | R
40204 | ActVArhQ3 | acc64 |  | unimplemented | R
40208 | ActVArhQ4 | acc64 |  | unimplemented | R
40212 | VArAval | int16 |  | unimplemented | R
40213 | VArAval_SF | sunssf |  | unimplemented | R
40214 | WAval | uint16 |  | unimplemented | R
40215 | WAval_SF | sunssf |  | unimplemented | R
40216 | StSetLimMsk | bitfield32 |  | unimplemented | R
|  |  | WMax | supported
|  |  | VAMax | supported
|  |  | VArAval | supported
|  |  | VArMaxQ1 | supported
|  |  | VArMaxQ2 | supported
|  |  | VArMaxQ3 | supported
|  |  | VArMaxQ4 | supported
|  |  | PFMinQ1 | supported
|  |  | PFMinQ2 | supported
|  |  | PFMinQ3 | supported
|  |  | PFMinQ4 | supported
40218 | StActCtl | bitfield32 |  | unimplemented | R
|  |  | FixedW | supported
|  |  | FixedVAR | supported
|  |  | FixedPF | supported
|  |  | Volt-VAr | supported
|  |  | Freq-Watt-Param | supported
|  |  | Freq-Watt-Curve | supported
|  |  | Dyn-Reactive-Current | supported
|  |  | LVRT | supported
|  |  | HVRT | supported
|  |  | Watt-PF | supported
|  |  | Volt-Watt | supported
|  |  | Scheduled | supported
|  |  | LFRT | supported
|  |  | HFRT | supported
40220 | TmSrc | string |  | supported | R
40224 | Tms | uint32 |  | supported | R
40226 | RtSt | bitfield16 |  | unimplemented | R
|  |  | LVRT_ACTIVE | supported
|  |  | HVRT_ACTIVE | supported
|  |  | LFRT_ACTIVE | supported
|  |  | HFRT_ACTIVE | supported
40227 | Ris | uint16 |  | supported | R
40228 | Ris_SF | sunssf |  | supported | R

## 123
Address | Point | Type | Subvalue | Value | R/W | Conformance Notes
40229 | ID | uint16 |  | 123
40230 | L | uint16 |  | 24
40231 | Conn_WinTms | uint16 |  | unimplemented | RW | Time window for connect/disconnect.
40232 | Conn_RvrtTms | uint16 |  | unimplemented | RW | Timeout period for connect/disconnect.
40233 | Conn | enum16 |  | supported | RW | Enumerated valued. Connection control. | Can be changed often!
|  |  | DISCONNECT | supported
|  |  | CONNECT | supported
40234 | WMaxLimPct | uint16 |  | supported | RW | Set power output to specified level. | Can be changed often!
40235 | WMaxLimPct_WinTms | uint16 |  | unimplemented | RW
40236 | WMaxLimPct_RvrtTms | uint16 |  | FW >1.00.10.R: supported | RW | Timeout period for active power limitation.
40237 | WMaxLimPct_RmpTms | uint16 |  | unimplemented | RW
40238 | WMaxLim_Ena | enum16 |  | supported | RW | Enumerated valued. Throttle enable/disable control. | Can be changed often!
|  |  | DISABLED | supported
|  |  | ENABLED | supported
40239 | OutPFSet | int16 |  | supported | RW | Set power factor to specific value - cosine of angle. | Can be changed often! Mutually exclusive to VAr registers!
40240 | OutPFSet_WinTms | uint16 |  | unimplemented | RW | Time window for power factor change.
40241 | OutPFSet_RvrtTms | uint16 |  | supported | RW | Timeout period for power factor.
40242 | OutPFSet_RmpTms | uint16 |  | unimplemented | RW | Ramp time for moving from current setpoint to new setpoint.
40243 | OutPFSet_Ena | enum16 |  | supported | RW | Enumerated valued. Fixed power factor enable/disable control. | Can be changed often! Mutually exclusive to OutPFSet registers.
|  |  | DISABLED | supported
|  |  | ENABLED | supported
40244 | VArWMaxPct | int16 |  | FW <1.00.10.R: supported FW >1.00.10.R: unimplemented | RW | Reactive power in percent of WMax. | Can be changed often! Mutually exclusive to OutPFSet registers.
40245 | VArMaxPct | int16 |  | FW <1.00.10.R: unimplemented FW >1.00.10.R: supported | RW | Reactive power in percent of VArMax. | Can be changed often! Mutually exclusive to OutPFSet registers.
40246 | VArAvalPct | int16 |  | unimplemented | RW | Reactive power in percent of VArAval. | Can be changed often! Mutually exclusive to OutPFSet registers.
40247 | VArPct_WinTms | uint16 |  | unimplemented | RW | Time window for VAR limit change.
40248 | VArPct_RvrtTms | uint16 |  | FW >1.00.10.R: supported | RW | Timeout period for VAR limit.
40249 | VArPct_RmpTms | uint16 |  | unimplemented | RW
40250 | VArPct_Mod | enum16 |  | unimplemented | RW
|  |  | NONE | unimplemented
|  |  | WMax | unimplemented
|  |  | VArMax | unimplemented
|  |  | VArAval | unimplemented
40251 | VArPct_Ena | enum16 |  | supported | RW | Enumerated valued. Percent limit VAr enable/disable control. | Can be changed often!
|  |  | DISABLED | supported
|  |  | ENABLED | supported
40252 | WMaxLimPct_SF | sunssf |  | supported | R | Scale factor for power output percent.
40253 | OutPFSet_SF | sunssf |  | supported | R | Scale factor for power factor.
40254 | VArPct_SF | sunssf |  | supported | R | Scale factor for reactive power percent.

## 160
Address | Point | Type | Subvalue | Value | R/W | Conformance Notes
41305 | ID | uint16 |  | 160
41306 | L | uint16 |  | 248
41307 | DCA_SF | sunssf |  | supported | R | Current Scale Factor
41308 | DCV_SF | sunssf |  | supported | R | Voltage Scale Factor
41309 | DCW_SF | sunssf |  | supported | R | Power Scale Factor
41310 | DCWH_SF | sunssf |  | unimplemented | R | Energy Scale Factor
41311 | Evt | bitfield32 |  | supported | R | Global Events
41313 | N | count |  | supported | R | Number of Modules
41314 | TmsPer | uint16 |  | unimplemented | R | Timestamp Period
Repeating block 12 MPPT (addresses +20 for every MPPT)
41315 | ID | uint16 |  | supported | R | Input ID
41323 | IDStr | string |  | unimplemented | R | Input ID Sting
41324 | DCA | uint16 |  | supported | R | DC Current
41325 | DCV | uint16 |  | supported | R | DC Voltage
41326 | DCW | uint16 |  | supported | R | DC Power
41328 | DCWH | acc32 |  | unimplemented | R | Lifetime Energy
41330 | Tms | uint32 |  | unimplemented | R | Timestamp
41331 | Tmp | int16 |  | unimplemented | R | Temperature
41332 | DCSt | enum16 |  | unimplemented | R | Operating State
41334 | DCEvt | bitfield32 |  | supported | R | Module Events

## SMA-specific
Firmware 1.00.xx.R | Firmware 1.01.xx.R
Address | Address | Point | Type | R/W
42893 | 42917 | Fault Code | uint 32 | R
43181 | 43205 | String 1 Current | uint 32 | R
43185 | 43209 | String 2 Current | uint 32 | R
43189 | 43213 | String 3 Current | uint 32 | R
43193 | 43217 | String 4 Current | uint 32 | R
43197 | 43221 | String 5 Current | uint 32 | R
43201 | 43225 | String 6 Current | uint 32 | R
43205 | 43229 | String 7 Current | uint 32 | R
43209 | 43233 | String 8 Current | uint 32 | R
43213 | 43237 | String 9 Current | uint 32 | R
43217 | 43241 | String 10 Current | uint 32 | R
43221 | 43245 | String 11 Current | uint 32 | R
43225 | 43249 | String 12 Current | uint 32 | R
43229 | 43253 | String 13 Current | uint 32 | R
43233 | 43257 | String 14 Current | uint 32 | R
43237 | 43261 | String 15 Current | uint 32 | R
43241 | 43265 | String 16 Current | uint 32 | R
43245 | 43269 | String 17 Current | uint 32 | R
43249 | 43273 | String 18 Current | uint 32 | R
43253 | 43277 | String 19 Current | uint 32 | R
43257 | 43281 | String 20 Current | uint 32 | R
43261 | 43285 | String 21 Current | uint 32 | R
43265 | 43289 | String 22 Current | uint 32 | R
43269 | 43293 | String 23 Current | uint 32 | R
43273 | 43297 | String 24 Current | uint 32 | R